| 项目名称 Project Name | TCC格鲁吉亚循环电站项目 Gardabani II Combined-Cycle Power Plant Project | 报告号 Report No. | CAPTCC-CT18008019 -IR01 |
| --- | --- | --- | --- |
| 客户 Client | 中国天辰工程有限公司 China Tianjin Engineering Corporation (TCC) | 客户订单号 Client P.O. No. | BP-T16B05-EQU-18029 |
| 检验通知号 Reference No. | BP-T16B05-EQU-18029 -PC14-IN-Rev.B | 检验员 Inspector | Pan guohua |
| 制造商 Vendor | Anhui Tian Kang (Group) shares Co.,Ltd | 检验地址 Inspection Location | Tianchang Economic Development Zone, Anhui |
| 分包商 Sub-Vendor | NA | 检验日期 Visit Date(s) | Aug 24th, 2018 |

| 本次检验参与人员 THE PARTICIPANTS OF THIS VISIT |
| --- |
| 姓名 NAME | 公司 COMPANY | 代表方 REPRESENTING | 联系方式 CONTACT NO. |
| Pan guohua | TCC | Inspector | 530518161@qq.com |
| Wang nibin | Anhui tiankang | Manager | 15249998661 |

| 本次检验产品 MATERIAL/ SUBJECT OF INSPECTION | 编号 Item No. | 订单数量 QTY as per P/O | 所检数量 QTY offered for inspection |
| --- | --- | --- | --- |
| Magnetic liquid level | 203/02LCM10CL500 | 1 | 1 |
| Magnetic liquid level | 203/02GHC40CL500 | 1 | 1 |
| Magnetic liquid level | 290/02PGB10CL500 | 1 | 1 |
| Magnetic liquid level | 290/02PGB34CL500 | 1 | 1 |
| Magnetic liquid level | 410/02GHD10CL500 | 2 | 2 |
| Magnetic liquid level | 410/02GKB10CL500 | 1 | 1 |
| Magnetic liquid level | 450/02GHC10CL500 | 1 | 1 |

| 适用文件 参考附件 REFERENCE DOCUMENTATION Refer to attachments instead |
| --- |
| 标题 Title | 文件编号 Reference No | 版本 Rev. | 批准状态 Approval status | 批准人 Approved by | 日期 Date |
| BP-T16B05-EQU-18029 | BP-T16B05-EQU-18029 | NA | NA | NA | 2018/07/31 |
| GBT 25153-2010 | GBT 25153-2010 | NA | NA | NA | 2011/03/01 |
| HGT 21584-1995 | HGT 21584-1995 | NA | NA | NA | 1995/11/01 |
| HGT 21584-1995 | HGT 21584-1995 | NA | NA | NA | NA |
| Drawing | NA | NA | NA | NA | 2018/07/17 |
| PACKING, MARKING AND SHIPPING INSTRUCTION | NA | NA | NA | NA | NA |
| ITP | BP-T16B05-EQU-18029-VD-2001 | 0 | Approval | NA | 2018/8/17 |

| ITP 相关 REFERENCE ITP |
| --- |
| 序号 S/N | 设备名称 Equipment/material | 检验项目 Inspection Activity (detail according to scope /standard/etc.) | 检验等级 Inspection Level H/W/SW/R | 相关文件 Relevant document |
| 1 | Magnetic liquid level | Hydrostatic pressure test | W | ITP |
| 2 | Magnetic liquid level | Visual inspection | W | ITP |
| 3 | Magnetic liquid level | Packing/Packing Procedure | W | ITP |

| 检验结果 INSPECTION RESULT |
| --- |
| 合格 Satisfactory (without comments) | 假释 Satisfactory with comments (Any of trailing punch or non-conformity items is still open) | 不合格 Not Satisfactory (NCR raised during the inspection) |
| 检验概述： SUMMARY Inspector review and sign the raw material certificate submitted by the factory, mechanical performance report, hydraulic test report, NDT test report, PMI report, Dimension inspection report, product warranty book, code sheet, The result was acceptable as per client specifications and ASME requirements. During his visit to the factory, the inspector witnessed the magnetic liquid level Hydrostatic pressure test. During the test, no leakage or deformation was found. The result accords with ASME Code Section VIII DIV 1 Inspector checked the defects on the magnetic liquid leve surface without cracks, scratches, holes and deformations.The result accords with ASME Code Section V/DIN EN 13018 Inspector is based on the packing procedure document.Inspection of packing terminals and packing list information is in line with the requirements. |
| 不符合项 Open Non Conformities | 是，详见不符合项表格 Yes, details in non-conformities | 无 No |
| 尾项清单 Open Punch List Items | 是,详见尾项情单表格 Yes, details in punch list | 无 No |
| 检验员签名 Inspector signature |  | 报告日期 Inspection report date | Aug 24th ,2018 |

| 不符合项 参考附件 NON CONFORMITIES Refer to attachments instead |
| --- |
| 项目 Item | 描述 Description | 状态 Status | 提出日期/报告号 Raised on/ Report # | 关闭日期/报告号 Closed on/ Report # | 备注 Comments |
| NA | NA | NA | NA | NA | NA | NA | NA |
| NA | NA | NA | NA | NA | NA | NA | NA |
| NA | NA | NA | NA | NA | NA | NA | NA |

| 尾项清单 参考附件 PUNCH LIST Refer to attachments instead |
| --- |
| 项目 Item | 描述 Description | 状态 Status | 提出日期/报告号 Raised on/ Report # | 关闭日期/报告号 Closed on/ Report # | 备注 Comments |
| NA | NA | NA | NA | NA | NA | NA | NA |
| NA | NA | NA | NA | NA | NA | NA | NA |

| 检验项目 THE ITEMS OF INSPECTION |
| --- |
| 预检会 Pre-inspection Meeting |  | 材料检验 Material Inspection |  | 数量检查 Quantity Check |  |
| 外观检验 Visual Inspection |  | 尺寸检验 Dimension Inspection |  | 试验见证 Test Witness |  |
| 防腐检验 Coating Inspection |  | 文件审核 Documents Review |  | 包装标识检验 Packing & Marking Inspection |  |
| 装车/船检验 Loading Inspection |  | 其他 Others |  |

检验详述 INSPECTION DETAILS

检验活动如下： Description of the inspections carried out: 材料检验MATERIALS INSPECTION Inspector checked the magnetic liquid leve material and the result was in line with the standard requirements. 数量检查QUANTITY CHECK Inspectors checked the number of magnetic liquid leve according to PO, and the results were consistent. 外观检验VISUAL INSPECTION Inspectors according to inspection requirements,Visual inspection magnetic liquid leve surface without cracks, scratches, pores, arc pits and deformations. gauge shall clear, smooth, clean, burrs free and injuries. The result accords with ASME Code Section V/DIN EN 13018 尺寸检验DIMENTION INSPECTION Inspector checked and signed the size inspection report submitted by the factory, and the result was acceptable. 防腐检验COATING INSPECTION NA 功能试验FUNCTIONAL AND PERFORMANCE TEST Before the inspector reviewed the valid certificate, the result is acceptable. Inspector witnessed the magnetic liquid level Hydrostatic pressure test.Test pressure: 3.0 Mpa; keep pressure for 30 minutes.No leakage and deformation. The result accords with ASME Code Section VIII DIV 1 In the process of float test, no flexibility was found in the turnover board, the result was acceptable. Details are as follows: Item Serial number QTY Prescribed value Pressure holding time Conclusion 1 203/02LCM10CL500 1 3.0 Mpa 30 Minutes Accept 2 203/02GHC40CL50 1 3.0 Mpa 30 Minutes Accept 3 290/02PGB10CL500 1 3.0 Mpa 30 Minutes Accept 4 290/02PGB34CL500 1 3.0 Mpa 30 Minutes Accept 5 410/02GHD10CL500 2 3.0 Mpa 30 Minutes Accept 6 410/02GKB10CL500 1 3.0 Mpa 30 Minutes Accept 7 450/02GHC10CL500 1 3.0 Mpa 30 Minutes Accept 特殊程序SPECIAL PROCESSES NA 包装和标识检验PACKING AND MARKING INSPECTION Inspector checked the packing according to the packing procedure documents provided.The result is acceptable. All box are made of export adhesive boards, which meet the requirements of ISPM15 standard. The surface of all containers has clear information on lifting, waterproofing, weight, transportation signs etc. All Magnetic liquid level are wrapped with waterproof plastic film, and the results are acceptable. Check the shipping marks and the packing list information is correct, there is 2 packing list on the outside of the box and 4 shipping marks on either side, 1 packing list on the inside of box. Inspector's inspection of shipping marks is acceptable. SHIPPING MARK: GARDABANI TCC PROJECT NO.：T16B05 DESTINATION：Construction site of Gardabani TPP2 Power Plant DESCRIPTION OF GOODS：Seamless Steel Pipe PACKAGE NO.: T16B05-AHTK-A-**/03 GROSS/NET WEIGHT(KG)：*** / *** kg MEASUREMENT (L*W*H IN CM) ***✖***✖*** CONSIGNOR：China Tianchen Engineering Corporation 装车/装船检验 LOADING INSPECTION NA 文件审查 DOCUMENTATION REVIEW Inspector review and sign the raw material certificate submitted by the factory, mechanical performance report, hydraulic test report, NDT test report, PMI report, Dimension inspection report, product warranty book, code sheet, The result was acceptable as per client specifications and ASME requirements. 放行/不符合项 RELEASE/NON-COMFORMANCE NA 健康安全/HEALTH AND SAFE Health & safety is in good condition, no accidents were occurred during this visit. 附件/ATTACHMENTS Attachment 1 CAPTCC -CT18008019-IR01- Photos Attachment 2 CAPTCC -CT18008019-IR01- Raw material certificate (MTC) and reinspection Report Attachment 3 CAPTCC -CT18008019-IR01- Dimension test report Attachment 4 CAPTCC -CT18008019-IR01- NDT test report Attachment 5 CAPTCC -CT18008019-IR01- PMI report Attachment 6 CAPTCC -CT18008019-IR01- Hydraulic test report Attachment 7 CAPTCC -CT18008019-IR01- Product qualification certificate Attachment 8 CAPTCC -CT18008019-IR01- Packing list Attachment 9 CAPTCC -CT18008019-IR01- MOM Attachment 10 CAPTCC -CT18008019-IR01- Effective certificate of testing equipment 下一次检验/NEXT VISIT NA

| 附件 ATTACHMENT |
| --- |
| 序号 Item | 附件名称 Attachment name | 描述 Description |
| 1 | CAPTCC-CT18008019-Photos | Inspection Photos |
| 2 | CAPTCC-CT18008019- Raw material certificate (MTC) and reinspection Report | Raw material certificate (MTC) and reinspection Report |
| 3 | CAPTCC-CT18008019- Dimension test report | Dimension test report |
| 4 | CAPTCC-CT18008019- NDT test report | NDT test report |
| 5 | CAPTCC-CT18008019- PMI report | PMI report |
| 6 | CAPTCC-CT18008005- Hydraulic test report | Hydraulic test report |
| 7 | CAPTCC-CT18008019- Product qualification certificate | Product qualification certificate |
| 8 | CAPTCC-CT18008019- Packing list | Packing list |
| 9 | CAPTCC-CT18008019- MOM | MOM |
| 10 | CAPTCC-CT18008019- Effective certificate of testing equipment | Effective certificate of testing equipment |

结束 End of Report