| 项目名称 Project Name | TCC格鲁吉亚循环电站项目 Gardabani II Combined-Cycle Power Plant Project | 报告号 Report No. | CAPTCC-CT18008048 -IR01 |
| --- | --- | --- | --- |
| 客户 Client | 中国天辰工程有限公司 China Tianjin Engineering Corporation (TCC) | 客户订单号 Client P.O. No. | BP-T16B05-MAT-EH-18005 |
| 检验通知号 Reference No. | CAPTCC-CT18008048 | 检验员 Inspector | Li yong |
| 制造商 Vendor | Jiangsu Sunbird Lighting Electrical Co.,LTD | 检验地址 Inspection Location | NO.48,Gongxinqiao Road,Xinba Town,Yangzhong City,Jiangsu Province |
| 分包商 Sub-Vendor | N/A | 检验日期 Visit Date(s) | Nov 16th.17th, 2018 |

| 本次检验参与人员 THE PARTICIPANTS OF THIS VISIT |
| --- |
| 姓名 NAME | 公司 COMPANY | 代表方 REPRESENTING | 联系方式 CONTACT NO. |
| Li yong | TCC | Inspector | 15062299494 |
| Ge wei | Jiangsu Sunbird | Manager | 13952906162 |

| 本次检验产品 MATERIAL/ SUBJECT OF INSPECTION | 编号 Item No. | 订单数量 QTY as per P/O | 所检数量 QTY offered for inspection |
| --- | --- | --- | --- |
| Fluorescent fixture 2x36W Ceiling Mounted | L9 | 19 | 19 |
| Fluorescent fixture 2x36W Mounted on Bracket | L9 | 96 | 96 |
| Emergency Fluorescent fixture 2x36W Ceiling Mounted | L9b | 21 | 21 |
| Emergency Fluorescent fixture 2x36W Mounted on Bracket | L9b | 9 | 9 |
| Recessed Fluorescent fixture 4x18W | L2 | 28 | 28 |
| Emergency Recessed Fluorescent fixture 4x18W | L2b | 2 | 2 |
| Corrosion-proof fluorescent lamp 1x32W Wall Mounted Corrosion-proof | L11 | 2 | 2 |
| Explosion-proof Fluorescent fixture 2x36W Mounted on Bracket | L12 | 4 | 4 |
| EXIT Luminaire | L6 | 9 | 9 |
| Fluorescent lamp hanger fittings | L9/L9b | 210 | 210 |
| Fluorescent tube 36W | L9/L9b/L12 | 300 | 300 |
| Fluorescent tube 18W | L2/L2b | 120 | 120 |
| Three protection fluorescent lamp wall fittings | L11 | 2 | 2 |

| 适用文件 参考附件 REFERENCE DOCUMENTATION Refer to attachments instead |
| --- |
| 标题 Title | 文件编号 Reference No | 版本 Rev. | 批准状态 Approval status | 批准人 Approved by | 日期 Date |
| Inspection notification | BP-T16B05-MAT-EH-18005-PC14-IN- Rev. A | / |  |  |  |
| Inspection and Test Plan | BP-T16B05-MAT-EH-18005 | / |  |  |  |
| Technical Agreement for Lighting Fixtures | T16B05-085EH82-030 | 0 | Approved | Li jing | 2018.10.16 |

| ITP 相关 REFERENCE ITP |
| --- |
| 序号 S/N | 设备名称 Equipment/material | 检验项目 Inspection Activity (detail according to scope /standard/etc.) | 检验等级 Inspection Level H/W/SW/R | 相关文件 Relevant document |
| 1 | 152 Unit lighting fixtures | Visual inspection and dimension check | SW | ITP-C1 |
| 2 | 152 Unit lighting fixtures | Marking inspection | SW | ITP-C2 |
| 3 | 152 Unit lighting fixtures | Pressure test | SW | ITP-C3 |
| 4 | 152 Unit lighting fixtures | Power test | SW | ITP-C4 |
| 5 | 152 Unit lighting fixtures | Ground resistance | SW | ITP-C5 |
| 6 | 152 Unit lighting fixtures | Protective performance test | SW | ITP-C6 |
| 7 | 152 Unit lighting fixtures | Packing | SW | ITP-C7 |
| 8 | 152 Unit lighting fixtures | Document review | R |  |

| 检验结果 INSPECTION RESULT |
| --- |
| 合格 Satisfactory (without comments) | 假释 Satisfactory with comments (Any of trailing punch or non-conformity items is still open) | 不合格 Not Satisfactory (NCR raised during the inspection) |
| 检验概述： SUMMARY Nov 16th to 17th TCC Inspector Visit Jiangsu Sunbird Lighting Electrical Co.,LTD; According to the notice of inspection, the inspection of the products is acceptable.Details are as follows: 1、Visual inspection and dimension check（ITP-C1） 1.1、Visual inspection According to the inspection requirements, the inspector lighting fixtures for the 10% of the visual inspection, found no pit, deformation and other defects. The result is able to accept. All lighting fixtures are plastic wrap and load within the carton.The results are acceptable. All fluorescent lamp load within the carton.The results are acceptable. 1.2、Dimension check According to the inspection requirements, the inspector recessed fluorescent fixture for the 10% of the dimension check, The result is able to accept. 2、Marking inspection（ITP-C2） Inspector checked the marking inspection for lighting fixtures,mark are the handwriting is clear and unmistakable.The result was acceptable. Pressure test（ITP-C3） Inspector checked 10% of lighting fixtures for the pressure test.Withstand voltage test 1500V, leakage current is not more than 5mA, time 3s.Meet standard requirements.The results are acceptable. Power test（ITP-C4） Inspector checked 10% of lighting fixtures for the power test.Voltage 220 v energizing test,the power error is less than 10%.Meet standard requirements.The results are acceptable. Ground resistance（ITP-C5） Inspector checked 10% of lighting fixtures for the ground resistance.10 a current,the Resistance is not more than 0.5 ohms.Meet standard requirements.The results are acceptable. Protective performance test（ITP-C6） Inspector checked 10% of lighting fixtures for the protective performance test.The lamps are placed in the rainwater test box and tested according to the requirements of the waterproof level. No water enters the waterproof ring of the lamp.Meet standard requirements.The results are acceptable. Packing（ITP-C7） 7.1、Inspector witnessed final inspection(packing/marking/shipment),All lighting fixtures USES the carton packaging, carton outside wrapped with waterproof membrane in the plywood case,which was in good appearance without damage or collision,The result was acceptable. 7.2、Inspector checked the packing(lighting fixtures)of cargos,plywood case solid and reliable,plywood case no damage or deformation.The factory mark is in the form of hot plastic sealing and pasted on the waterproof cloth.The result was acceptable. 7.3、Inspector checked items mark,all cargos mark clear and unmistakable.The result was acceptable. Document review Review the product qualification certificate of lighting fixtures, lighting fixtures inspection report, packing list, etc.The results are acceptable. |
| 不符合项 Open Non Conformities | 是，详见不符合项表格 Yes, details in non-conformities | 无 No |
| 尾项清单 Open Punch List Items | 是,详见尾项情单表格 Yes, details in punch list | 无 No |
| 检验员签名 Inspector signature |  | 报告日期 Inspection report date | Nov.17.2018 |

| 不符合项 参考附件 NON CONFORMITIES Refer to attachments instead |
| --- |
| 项目 Item | 描述 Description | 状态 Status | 提出日期/报告号 Raised on/ Report # | 关闭日期/报告号 Closed on/ Report # | 备注 Comments |

| 尾项清单 参考附件 PUNCH LIST Refer to attachments instead |
| --- |
| 项目 Item | 描述 Description | 状态 Status | 提出日期/报告号 Raised on/ Report # | 关闭日期/报告号 Closed on/ Report # | 备注 Comments |

| 检验项目 THE ITEMS OF INSPECTION |
| --- |
| 预检会 Pre-inspection Meeting |  | 材料检验 Material Inspection |  | 数量检查 Quantity Check |  |
| 外观检验 Visual Inspection |  | 尺寸检验 Dimension Inspection |  | 试验见证 Test Witness |  |
| 防腐检验 Coating Inspection |  | 文件审核 Documents Review |  | 包装标识检验 Packing & Marking Inspection |  |
| 装车/船检验 Loading Inspection |  | 其他 Others |  |

检验详述 INSPECTION DETAILS

检验活动如下： Description of the inspections carried out: 材料检验MATERIALS INSPECTION N/A 数量检查QUANTITY CHECK TCC inspector performed quantity for 1 packages. The inspectors randomly checked the quantity, and the result was acceptable with the packing list from factory. 外观检验VISUAL INSPECTION According to the inspection requirements,the inspector lighting fixtures for the 10% of the visual inspection,found no pit, deformation and other defects.The result is able to accept. All lighting fixtures are plastic wrap and load within the carton.The results are acceptable. All fluorescent lamp load within the carton.The results are acceptable. 尺寸检验DIMENTION INSPECTION According to the inspection requirements,the inspector recessed fluorescent fixture for the 10% of the dimension check,Recessed fluorescent fixture size meet the requirements of the installation of 600*600.The result is able to accept. 防腐检验COATING INSPECTION N/A 功能试验FUNCTIONAL AND PERFORMANCE TEST 6.1、Pressure test Inspector checked 10% of lighting fixtures for the pressure test.Withstand voltage test 1500V, leakage current is not more than 5mA, time 3s.Meet standard requirements.The results are acceptable. 6.2、Power test Inspector checked 10% of lighting fixtures for the power test.Voltage 220 v energizing test,the power error is less than 10%.Meet standard requirements.The results are acceptable. 6.3、Ground resistance Inspector checked 10% of lighting fixtures for the ground resistance.10 a current,the Resistance is not more than 0.5 ohms.Meet standard requirements.The results are acceptable. 6.4、Protective performance test Inspector checked 10% of lighting fixtures for the protective performance test.The lamps are placed in the rainwater test box and tested according to the requirements of the waterproof level. No water enters the waterproof ring of the lamp.Meet standard requirements.The results are acceptable. 特殊程序SPECIAL PROCESSES N/A 包装和标识检验PACKING AND MARKING INSPECTION 8.1、Marking inspection Inspector checked the marking inspection for lighting fixtures,mark are the handwriting is clear and unmistakable.The result was acceptable. 8.2、Packing inspection Inspector witnessed final inspection(packing/marking/shipment),All lighting fixtures USES the carton packaging, carton outside wrapped with waterproof membrane in the plywood case,which was in good appearance without damage or collision,The result was acceptable. Inspector checked the packing(lighting fixtures)of cargos,plywood case solid and reliable,plywood case no damage or deformation.The factory mark is in the form of hot plastic sealing and pasted on the waterproof cloth.The result was acceptable. Inspector checked items mark,all cargos mark clear and unmistakable.The result was acceptable. 装车/装船检验 LOADING INSPECTION N/A 文件审查 DOCUMENTATION REVIEW Review the product qualification certificate of lighting fixtures, lighting fixtures inspection report, packing list, etc.The results are acceptable. 放行/不符合项 RELEASE/NON-COMFORMANCE RELEASE 健康安全/HEALTH AND SAFE N/A 附件/ATTACHMENTS See the attachment 下一次检验/NEXT VISIT N/A

| 附件 ATTACHMENT |
| --- |
| 序号 Item | 附件名称 Attachment name | 描述 Description |
| 1 | CAPTCC-CT18008048 -IR01-Photos | Inspection Photos |
| 2 | CAPTCC-CT18008048 -IR01-MOM | MOM |
| 3 | CAPTCC-CT18008048 -IR01-Certificate | Certificate |
| 4 | CAPTCC-CT18008048 -IR01-Incoming inspection record | Incoming inspection record |
| 5 | CAPTCC-CT18008048 -IR01-Routine inspection record | Routine inspection record |
| 6 | CAPTCC-CT18008048 -IR01-Packing list | Packing list |
| 7 | CAPTCC-CT18008048 -IR01-IRN01 | Inspection Release note |

结束 End of Report