| 项目名称 Project Name | Gardabani II Combined-Cycle Power Plant Project | 报告号 Report No. | CAPTCC-CT18008058-IR03 |
| --- | --- | --- | --- |
| 客户 Client | China Tianchen Engineering Corporation | 客户订单号 Client P.O. No. | BP-T16B05-EQU-EH-18012 |
| 检验通知号 Reference No. | "BP-T16B05-EQU-EH-18012"-PC14-IN- Rev. C | 检验员 Inspector | Han Yuhong |
| 制造商 Vendor | WARON TECHNOLOGY INCORPORATED COMPANY | 检验地址 Inspection Location | No.555#Baoqian Road,Jiading,Shanghai, PRC |
| 分包商 Sub-Vendor |  | 检验日期 Visit Date(s) | 16th .Jan, 2019 |

| 本次检验参与人员 THE PARTICIPANTS OF THIS VISIT |
| --- |
| 姓名 NAME | 公司 COMPANY | 代表方 REPRESENTING | 联系方式 CONTACT NO. |
| Peng Mingchao | Shanghai Waron | Vendor | / |
| Han Yuhong | CAPTCC | TCC/EPC | / |

| 本次检验产品 MATERIAL/ SUBJECT OF INSPECTION | 编号 Tag No. | 订单数量 QTY as per P/O | 所检数量 QTY offered for inspection |
| --- | --- | --- | --- |
| Terminal box | 17 | 1 | / |
| Terminal box | 18 | 1 | / |
| Terminal box | 19 | 1 | / |
| Terminal box | 20 | 1 | / |
| Terminal box | 21 | 1 | / |
| Power distribution | 22 | 1 | 1 |
| Power distribution | 23 | 1 | 1 |
| Power distribution | 24 | 1 | 1 |
| Power distribution | 25 | 1 | 1 |
| Power distribution | 26 | 1 | / |
| Power distribution | 27 | 1 | 1 |
| Power distribution | 28 | 1 | 1 |
| Power distribution | 29 | 1 | 1 |
| Power distribution | 30 | 1 | 1 |
| Power distribution | 32 | 1 | 1 |
| Power distribution | / | 1 | 1 |
| Cable transfer | / | 1 | 1 |
| Total | 17 | 11 |  |

| 适用文件 参考附件 REFERENCE DOCUMENTATION Refer to attachments instead |
| --- |
| 标题 Title | 文件编号 Reference No | 版本 Rev. | 批准状态 Approval status | 批准人 Approved by | 日期 Date |
| Technical Agreement | T16B05-85EH82-029 | 0 | Approved | TCC | / |
| ASTM A240 |  | 2010 |  |  |  |

| ITP 相关 REFERENCE ITP |
| --- |
| 序号 S/N | 设备名称 Equipment/material | 检验项目 Inspection Activity (detail according to scope /standard/etc.) | 检验等级 Inspection Level H/W/SW/R | 相关文件 Relevant document |
| 1 | Distribution Panel | Appearance Inspection | W |  |
| 2 | Distribution Panel | Package | W |  |
| 3 | Distribution Panel | Quality Documents Review | R |  |

| 检验结果 INSPECTION RESULT |
| --- |
| 合格 Satisfactory (without comments) | 假释 Satisfactory with comments (Any of trailing punch or non-conformity items is still open) | 不合格 Not Satisfactory (NCR raised during the inspection) |
| 检验概述： SUMMARY Visited WARON Shanghai Factory performed the final inspection as per approved technical agreement and inspection notification, the results conform to technical agreement requirements but the packing and marking were unfinished. WARON reply that they will provide photos for marking and packing to review once finished packing. |
| 不符合项 Open Non Conformity | 是，详见不符合项表格 Yes, details in non-conformity | 无 No |
| 尾项清单 Open Punch List Items | 是,详见尾项清单表格 Yes, details in punch list | 无 No |
| 检验员签名 Inspector signature | Han Yuhong | 报告日期 Inspection report date | Jan 17, 2019 |

| 不符合项参考附件 NON CONFORMITIES Refer to attachments instead |
| --- |
| 项目 Item | 描述 Description | 状态 Status | 提出日期/报告号 Raised on/ Report | 关闭日期/报告号 Closed on/ Report # | 备注 Comments |
| NA | NA |  |  |  |  |  |  |

| 尾项清单 参考附件 PUNCH LIST Refer to attachments instead |
| --- |
| 项目 Item | 描述 Description | 状态 Status | 提出日期/报告号 Raised on/ Report # | 关闭日期/报告号 Closed on/ Report # | 备注 Comments |
| 1 | Packing work not finished when inspector left Waron. Waron need to supply packing photos for review. | open | 1.17 | IR03 |  |  |  |

| 检验项目 THE ITEMS OF INSPECTION |
| --- |
| 预检会 Pre-inspection Meeting |  | 材料检验 Material Inspection |  | 数量检查 Quantity Check |  |
| 外观检验 Visual Inspection |  | 尺寸检验 Dimension Inspection |  | 试验见证 Test Witness |  |
| 防腐检验 Coating Inspection |  | 文件审核 Documents Review |  | 包装标识检验 Packing & Marking Inspection |  |
| 装车/船检验 Loading Inspection |  | 其他 Others |  |

检验详述 INSPECTION DETAILS

检验活动如下： Description of the inspection activities carried out: Appearance inspection (Clause 03 of ITP) Inspector carried out the visual quality inspection for 17pcs distribution boxes including marks, tags, appearance surface and type of electrical components, painting color. The result was acceptable. Quantity inspection There were 17pcs distribution boxes on site. The result was acceptable as per the third batch products list of Supply. Item26 (1pc distribution Box) lack of an assembly and item17~21 (5pcs distribution Boxes) were unfinished assembling. WARON reply that they will provide photos for marking and packing to review once finished packing. Packing and Marking Inspection(Clause 04 of ITP) Inspector performed packing inspection, the products were put in plastic bag and then placed in plywood case as per the Packing, Marking and Shipping instruction. There was 11pcs distribution Boxes finished packing on site. The result was acceptable. Reviewed documents Reviewed and signed off product inspection report including raw materials certifications and certification of quality.

| 附件 ATTACHMENT |
| --- |
| 序号 Item | 附件名称 Attachment name | 描述 Description |
| 1 | CAPTCC-CT18008058-IR03-Photos | Inspection Photos |
| 2 | CAPTCC-CT18008058-MOM03 | MOM |
| 3 | Certification Of Quality | Certification Of Quality |
| 4 | Production Inspection Report | Production Inspection Report |
| 5 | Product Test Report | Product Test Report |

结束 End of Report